## Slide 1
KERIS 5.1
220/277/347/400/440/480V
0686_5010_B
1
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
50-60 Hz
IK 08
IP 66
Indicator tip pointing towards the surface to be lit
KERIS 5.1
Important: if the power supply is >250V and a remote management system is used, make sure it supports the supply voltage (for example: Wizard Nema does not support voltages > 250V)
Available with built-in power supply, see page 13
KERIS 5.1 |  | SCx |  |  |  |  |  |  |  |  |  |  | H max
 | 9 kg without power supply | Pitch | 0° | 10° | 20° | 30° | 40° | 50° | 60° | 70° | 80° | 90° | 30 m
 |  | SCx (m2) (without power supply) | 0.04 | 0.06 | 0.08 | 0.11 | 0.12 | 0.14 | 0.15 | 0.16 | 0.17 | 0.17 | 
 | Power supply 3.1 kg | SCx (m2) (with power supply) | 0.06 | 0.08 | 0.09 | 0.11 | 0.13 | 0.15 | 0.17 | 0.18 | 0.2 | 0.2 | 

## Slide 2
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
2
SUSPENDED
WALL MOUNTED
SUPPORTED
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 3
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
3
2x M10 screws
18 N.m
+
2x L10 washers
Screws and washers not included
(Use hardware treated
against corrosion)
FIXING
1x M12 screw
27 N.m
+
1x L12 washer
+ safety line
Screws, washers and line not included
(Use hardware treated
against corrosion)
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
2 fixings are required as per the EN60598-2-3 standard

## Slide 4
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
4
DIRECTIONAL ADJUSTMENT
FITTING A SIGHT
1
2
1
2
3
Right position
Left position
Attach the sight’s safety line to the floodlight.
4
0 | 3 | 4 | 5 | 6
PFI - PFM | ASY 30 | ASY 40 | ASY 50 | "-"
The sight must be adjusted according to the optics and/or the adjustment plane. Regardless of the sight position on the floodlight, the angular adjustment is positive towards the front of the projector for positions 3, 4, 5 and 6.
1
2
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 5
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
5
PITCH ADJUSTMENT
1
2
WIRING
12 N.m
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 6
6
WIRING
MAINS
OUTPUT
DALI
MODULE EARTH
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
 | Cable gland | Cable Ømin mm | Cable Ømax mm | Tightening torque N.m | Cable example | Size mm2
Mains | PG13.5 | 6 | 11 | 1.4 | HO7RN-F 450V/750V | 1.5-2.5
Between power supply and floodlight (output) | PG19 | 8 | 12 | 2.4 | HO7RN-F 450V/750V | 1.5-2.5
DALI | PG9 | 4.5 | 8 | 1 | HO7RN-F 450V/750V | 1.5

## Slide 7
Flat-tipped screwdriver size 3 to 3.5
7
1
4
2
3
4x
DRIVER CONNECTION TERMINAL BLOCK
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
8 to 9 mm

## Slide 8
8
Wiring diagram with remote power supply:
Mains power supply
Max cable Ø: 11 mm
Min cable Ø: 6 mm
Cross section: 2.5 mm² max
Size: 3*2.5 mm² max
(Max length: 200 m for 3*2.5 mm²
Max length: 196 m for 3*1.5 mm²)
Max cable Ø: 12 mm
Min cable Ø: 8 mm
3 wires:
Brown: module +
Blue module -
Y/G: ground
Cable not supplied by ECLATEC
Cable not supplied by ECLATEC
Connector supplied by ECLATEC
Respect the connection order
Power supply supplied by ECLATEC
Connect and tighten the 2 ties
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 9
9
Wiring diagram with remote power supply, DALI version
with ECLATEC control box:
DALI max length 300 m
=> control box
DALI wires
Max cable Ø: 10 mm
Min cable Ø: 5 mm
Cross section: 2.5 mm² max
Size: 3*2.5 mm² max
(Max length: 200 m for 3*2.5 mm²
Max length: 196 m for 3*1.5 mm²)
Max cable Ø: 12 mm
Min cable Ø: 8 mm
3 wires:
Brown: module +
Blue module -
Y/G: ground
To contactor 1
½ stadium right
Max cable Ø: 11 mm
Min cable Ø: 6 mm
Cross section: 2.5 mm² max
To contactor 2
½ stadium left
Max cable Ø: 11 mm
Min cable Ø: 6 mm
Cross section: 2.5 mm² max
Cables not supplied by ECLATEC
Cables not supplied by ECLATEC
Cables not supplied by ECLATEC
Cables not supplied by ECLATEC
Connector supplied by ECLATEC
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 10
10
POWER SUPPLY INSTALLATION IN A CABINET
The power supplies must be installed in the vertical position
After installation, it is recommended to measure the Tc temperatures which must not exceed the values given in the table.
Move the power supplies apart or force the ventilation if necessary.
Tc
Ambient T
The ambient temperature must be measured between 2 power supplies
3.1 kg
134
58.6
335
4 x Ø7 mm
291 mm
128.9 mm
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 11
11
POLE FOOT INSTALLATION
Part number1 and hardware supplied with the remote power supply option
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
5 | 1 | ENEDO 600W POWER SUPPLY |  | 
4 | 2 | STAINLESS STEEL H6 NUT | 8331150100 | 
3 | 2 | STAINLESS STEEL 6 CONTACT WASHER | 8321551100 | 
2 | 2 | STAINLESS STEEL CHC M6X20-20 | 8311652000 | 
1 | 1 | SPL POLE FOOT COMPATIBLE WITH KERIS 5.1/5.2/6 | 7432452710 | 0686_0088
PART NO | QTY | NAME | CODE | DRAWING

## Slide 12
CLEANING
Remove physical elements that can block and modify air cooling (radiator fins).
Cleaning frequency (depends on the installation location and environment).
Always test the sample with the cleaning product using the selected technique first.
Do not leave cleaning products on the plastic parts for long periods of time.
Do not apply cleaning products in direct sunlight or at high temperatures.
Glass part cleaning.
Recommended cleaning products:
Mild soap.
Warm water.
Soft cloth/no abrasives.
Sponge.
Cleaning with water.
Pollution can significantly alter luminaire lighting performances.
We recommend regular cleaning of the module reflectors and to check that the radiators are not obstructed.
TRIGGER CURRENT
12
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 13
Built-in power supply version – Fixing the power supply to the bracket
13
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
SUSPENDED VERSION
WALL-MOUNTED VERSION
SUPPORTED VERSION
IMPORTANT, THE POWER SUPPLY SUPPORT IS DIFFERENT FOR THE WALL-MOUNTED VERSION (THE HARDWARE REMAINS THE SAME):
KERIS 5-1 WALL-MOUNTED POWER SUPPLY SUPPORT
DRAWING 0686_0111

## Slide 14
Built-in power supply version – Fixing the power supply to the bracket
14
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
Screw kit for the
supported/suspended version
Screw kit for the wall-mounted version
OR
IMPORTANT There are 2 power supply support references depending on the floodlight position
This choice was made when the order was entered
KERIS 5-1 SUPPORTED AND SUSPENDED POWER SUPPLY SUPPORT
1
KERIS 5-1 WALL-MOUNTED POWER SUPPLY SUPPORT
1
5 | 4 | STAINLESS STEEL CHC M6X20-20 | 8311652000 | 
4 | 8 | STAINLESS STEEL H6 NUT | 8331150100 | 
3 | 8 | STAINLESS STEEL WASHER CS 6-14-1.3 25-511 | 8321551100 | 
2 | 4 | STAINLESS STEEL FCH 6x20 SCREW | 8311612000 | 
1 | 2 | KERIS 5-1 SUPPORTED AND SUSPENDED POWER SUPPLY SUPPORT |  | 
PART NO | QTY | NAME | CODE | DRAWING