## Slide 1
KERIS 5.2 & 6
INVENTRONICS
220-415V 47-63 Hz
0686_5003_B
KERIS 5.2
KERIS 6
KERIS 6
KERIS 5.2
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
IK 08
IP 66
Indicator tip pointing towards the surface to be lit
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 2
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
The floodlights are identified by a coloured label showing the type of light distribution.
Position the floodlights on the support, making sure to use the colour indicated in the settings plan.
YELLOW LABEL ASY 30-N-1
BLUE LABEL ASY 30-M-1
RED LABEL ASY 30-W-1
GREEN LABEL ASY 40-M-1
PINK LABEL ASY 65-M-1
PURPLE LABEL P-FM-1
ORANGE LABEL P-FI-1
Example
Example

## Slide 3
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
4 x Ø8.5 mm
134mm
480mm
10.5mm
653 max
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
90
: 7 kg
(with fasteners)

## Slide 4
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
Suspended advanced
Supported advanced
PITCH/CONFIGURATION POSSIBILITIES
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
EMBEDDED POWER SUPPLY |  | 
 | A | B
TYPE 1 DOOR |  | 
TYPE 1 SUSPENDED |  | 
TYPE 2 |  | 
FLOODLIGHT POSITION
ON BRACKET
TYPE
FLOODLIGHT FIXTURE
OFFSET POWER SUPPLY |  | 
 | A | B
TYPE 1 DOOR |  | 
TYPE 1 SUSPENDED |  | 
TYPE 2 |  | 
TYPE
FLOODLIGHT FIXTURE
FLOODLIGHT POSITION
ON BRACKET

## Slide 5
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
1x M20 screw
100 N.m
+
LL20 washer
(Ø60xth.3)
Screws and washers not included
(Use hardware treated
against corrosion)
2x M16 screws
65 N.m
+
2x LL16 washers
(Ø50xth.3)
Screws and washers not included
(Use hardware treated
against corrosion)
100
200
Attach a safety line around the bracket arm. Line not included
FIXING
3
OR
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 6
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
DIRECTIONAL ADJUSTMENT
FITTING A SIGHT
1
2
1
2
3
Upper Right Module Position
Lower Right Module Position
Upper Left Module Position
Lower Left Module Position
Attach the sight’s safety line to the floodlight.
4
0 | 3 | 4 | 5 | 6
PFI - PFM | ASY 30 | ASY 40 | ASY 50 | "-"
The sight must be adjusted according to the optics and/or the adjustment plane. Regardless of the sight position on the floodlight, the angular adjustment is positive towards the front of the projector for positions 3, 4, 5 and 6.
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 7
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
1
5
3
3
12 N.m
2
50 N.m
4
PITCH ADJUSTMENT
Operations to carry out on both sides
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 8
La source lumineuse contenue dans ce luminaire ne doit être remplacée que par le fabricant ou son agent de maintenance ou une personne de qualification équivalente.
The lighting part included in this luminaire must be maintained by the manufacturer, an authorised service agent or a person with similar technical qualification.
1
2
3
x4
2
1
2
3
4
100mm
1
SWITCHING FROM POSITION A TO B
Operations to carry out on both sides
Operations to carry out on both sides
SWITCHING FROM TYPE 1 TO TYPE 2 POSITION
SEE MANUAL NO0686_5005
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
A
B

## Slide 9
1
2
3
1
x4
2
Module 1
Module 2
Module 3
WIRING
Cover
1
2
3
4
5
6
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 10
DRIVER CONNECTION TERMINAL BLOCK
Flat-tipped screwdriver size 3 to 3.5
8 to 9 mm
1
4
2
3
4x
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
The driver complies with the D4i standard
with the DALI supply bus activated.
* P/E M25 for cable 1.5-2.5² Ø13 to Ø18mm
-If the cable diameter is smaller, Ø9 to Ø13mmm, replace the cable gland with the one supplied in the electric connection compartment
Cable gland for Ø13 to Ø18 cable
Cable gland for Ø9 to Ø13 cable
The photo shows the cable gland direction. Push it in as far as it will go
Figure 2 Tension spring connection
Connecting the conductors
Strip the conductors over the indicated length. 8 to 9 mm
Flexible conductors can be fitted with terminal ends.
Crimp the terminal ends using crimping pliers. Make sure the DIN 46228-4 standard test requirements are met.
The terminal end length must match the stripped length of the conductor.
To open the connection point, insert a screwdriver into the rectangular opening.
Flat-tipped screwdriver size 3 to 3.5
Insert the conductor into the round connection opening as far as it will go.
Remove the screwdriver to make the conductor connection.
To release the conductor, insert the screwdriver into the opening again.

## Slide 11
INPUT
3 a
POWER SUPPLY WIRING
Cover
KERIS 6 Module 2
KERIS 6 Module 3
KERIS 5.2 Module 2
Module 1
KERIS 5.2 AND 6
KERIS 5.2 NTC module 2
1
2
3
4
5
6
5
2
1
3
KERIS 5.2 and 6
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
4
CM
L1
PE
DA+
DA-
L2
24V
SHD
LUM
V1+
V1-
V2+
V2-
V3+
V3-
OTP
DA+
DA-
POWER SUPPLY/FLOODLIGHT WIRING
Using 7G1.5 cable, connect wire "6" to the "WAGO 221" terminal block, which will be connected to terminals 2+ and 3+ using 1mm² wire.
For a larger cross section 7G cable, an external connection will have to be made. (Contact us)
Cable gland
Tightening torque
N.m
Cable diameter
mm
AWG
Cable
Cable
Size
mm
9-18
6
OUTPUT

## Slide 12
INPUT
3b
POWER SUPPLY WIRING WITH THE DALI PROTOCOL
Cover
KERIS 6 Module 2
KERIS 6 Module 3
KERIS 5.2 Module 2
Module 1
KERIS 5.2 AND 6
KERIS 5.2 NTC module 2
1
2
3
4
5
6
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
5
2
1
3
KERIS 5.2 and 6
4
CM
L1
PE
DA+
DA-
L2
24V
SHD
LUM
V1+
V1-
V2+
V2-
V3+
V3-
OTP
DA+
DA-
Cable gland
Tightening torque
N.m
Cable diameter
mm
AWG
Cable
Cable
Size
mm
9-18
6
OUTPUT
POWER SUPPLY/FLOODLIGHT WIRING
Using 7G1.5 cable, connect wire "6" to the "WAGO 221" terminal block, which will be connected to terminals 2+ and 3+ using 1mm² wire.
For a larger cross section 7G cable, an external connection will have to be made. (Contact us)
OUTPUT
INPUT

## Slide 13
3c
POWER SUPPLY WIRING WITH THE DMX PROTOCOL
Cover
KERIS 6 Module 2
KERIS 6 Module 3
KERIS 5.2 Module 2
Module 1
KERIS 5.2 AND 6
KERIS 5.2 NTC module 2
1
2
3
4
5
6
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
INPUT
5
2
1
KERIS 5.2 and 6
4
CM
L1
PE
DA+
DA-
L2
24V
SHD
LUM
V1+
V1-
V2+
V2-
V3+
V3-
OTP
DA+
DA-
Cable gland
Tightening torque
N.m
Cable diameter
mm
AWG
Cable
Cable
Size
mm
9-18
6
OUTPUT
3
POWER SUPPLY/FLOODLIGHT WIRING
Using 7G1.5 cable, connect wire "6" to the "WAGO 221" terminal block, which will be connected to terminals 2+ and 3+ using 1mm² wire.
For a larger cross section 7G cable, an external connection will have to be made. (Contact us)

## Slide 14
3d
POWER SUPPLY WIRING WITH THE D4i PROTOCOL
Cover
KERIS 6 Module 2
KERIS 6 Module 3
KERIS 5.2 Module 2
Module 1
KERIS 5.2 AND 6
KERIS 5.2 NTC module 2
1
2
3
4
5
6
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
5
2
1
3
KERIS 5.2 and 6
4
CM
L1
PE
DA+
DA-
L2
24V
SHD
LUM
V1+
V1-
V2+
V2-
V3+
V3-
OTP
DA+
DA-
Cable gland
Tightening torque
N.m
Cable diameter
mm
AWG
Cable
Cable
Size
mm
+
-
9-18
6
OUTPUT
POWER SUPPLY/FLOODLIGHT WIRING
Using 7G1.5 cable, connect wire "6" to the "WAGO 221" terminal block, which will be connected to terminals 2+ and 3+ using 1mm² wire.
For a larger cross section 7G cable, an external connection will have to be made. (Contact us)
INPUT
OUTPUT
INPUT
-
+
24V

## Slide 15
DALI/DMX
M16
OUTPUT
M32
VENTILATION
VALVE
WATERPROOF
PLUG
DALI/DMX RELAUNCH
M16
INPUT
M25
DALI/DMX
M16
OUTPUT
M32
VENTILATION
VALVE
WATERPROOF
PLUG
DALI/DMX RELAUNCH
M16
INPUT
M25
Wiring diagram with remote power supply:
230 V or 400 V mains power supply
Max cable Ø: 17mm
Min cable Ø: 10mm
Cross section: 4 mm² max
KERIS 6
Cross section: 7*2.5 mm² max
Max length: 200 m for 7*2.5 mm²
Max length: 100 m for 7*1.5 mm²
Max cable Ø: 21mm
Min cable Ø: 11mm
7 wires:
Wire 1: NTC PCB
Wire 2: -1 LED
Wire 3: -2 LED
Wire 4: -3 LED
Wire 5: +1 LED
Wire 6: +2 & 3+ LED
Y/G: ground
KERIS 5.2
Cross section: 6*2.5 mm² max
Max length: 200 m for 6*2.5 mm²
Max length: 100 m for 6*1.5 mm²
Max cable Ø: 21mm
Min cable Ø: 11mm
6 wires:
Wire 1: NTC PCB
Wire 2: -1 LED
Wire 3: -2 LED
Wire 4: +1 LED
Wire 5: +2 LED
Y/G: ground
Wiring diagram with power supply not built into the floodlights:
230 V or 400 V mains power supply
Max cable Ø: 17mm
Min cable Ø: 10mm
Cross section: 4 mm² max
Cables not supplied by ECLATEC
Cables not supplied by ECLATEC
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 16
OUTPUT
M32
VENTILATION
VALVE
WATERPROOF
PLUG
DALI/DMX RELAUNCH
M16
INPUT
M25
Wiring diagram with remote power supply, DALI version
and
ECLATEC control box:
To contactor 1
½ stadium right
Max cable Ø: 17mm
Min cable Ø: 10mm
Cross section: 4 mm² max
To contactor 2
½ stadium left
Max cable Ø: 17mm
Min cable Ø: 10mm
Cross section: 4 mm² max
DALI max length 300 m
=> control box
DALI wires
Max cable Ø: 10mm
Min cable Ø: 5mm
Cross section: 2.5 mm² max
Cables not supplied by ECLATEC
KERIS 6
Cross section: 7*2.5 mm² max
Max length: 200 m for 7*2.5 mm²
Max length: 100 m for 7*1.5 mm²
Max cable Ø: 21mm
Min cable Ø: 11mm
7 wires:
Wire 1: NTC PCB
Wire 2: -1 LED
Wire 3: -2 LED
Wire 4: -3 LED
Wire 5: +1 LED
Wire 6: +2 & 3+ LED
Y/G: ground
KERIS 5.2
Cross section: 6*2.5 mm² max
Max length: 200 m for 6*2.5 mm²
Max length: 100 m for 6*1.5 mm²
Max cable Ø: 21mm
Min cable Ø: 11mm
6 wires:
Wire 1: NTC PCB
Wire 2: -1 LED
Wire 3: -2 LED
Wire 4: +1 LED
Wire 5: +2 LED
Y/G: ground
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
DALI/DMX
M16
OUTPUT
M32
VENTILATION
VALVE
WATERPROOF
PLUG
DALI/DMX RELAUNCH
M16
INPUT
M25
DALI/DMX
M16

## Slide 17
OUTPUT
M32
VENTILATION
VALVE
WATERPROOF
PLUG
DALI/DMX RELAUNCH
M16
INPUT
M25
DALI/DMX
M16
Wiring diagram with remote power supply built into the floodlights and DALI version
and
ECLATEC control box:
Cables not supplied by ECLATEC
DALI max length 300 m
=> control box
DALI wires
Max cable Ø: 10mm
Max cable Ø: 5mm
Cross section: 2.5 mm² max
To contactor 1
½ stadium right
Max cable Ø: 17mm
Min cable Ø: 10mm
Cross section: 6 mm² max
To contactor 2
½ stadium left
Max cable Ø: 17mm
Min cable Ø: 10mm
Cross section: 6 mm² max
DALI wires
Max cable Ø: 10mm
Max cable Ø: 5mm
Cross section: 2.5 mm² max
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
OUTPUT
M32
VENTILATION
VALVE
WATERPROOF
PLUG
DALI/DMX RELAUNCH
M16
INPUT
M25
DALI/DMX
M16

## Slide 18
POWER SUPPLY INSTALLATION IN A CABINET
The distance between the control boxes and the side walls is recommended as shown in the drawing.
Carry out thermal tests in real installation and application conditions and guarantee that the box temperature is below 80°C guaranteed Tc.
It is suggested that you select a painted cabinet enclosure with a high reflectance ratio to reduce solar radiant heat.
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com

## Slide 19
POLE FOOT INSTALLATION
Part number1 and hardware supplied with the remote power supply option
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
525
480
500
90
134
65
210
5 | 2 | STAINLESS STEEL H8 NUT
4 | 2 | STAINLESS STEEL 8 CONTACT WASHER
3 | 2 | STAINLESS STEEL CHC M8X20-20
2 | 1 | POWER SUPPLY
1 | 1 | SPL KERIS 5-6 POLE FOOT
PART NO | QTY | NAME

## Slide 20
CLEANING
Remove physical elements that can block and modify air cooling (radiator fins).
Cleaning frequency (depends on the installation location and environment).
Always test the sample with the cleaning product using the selected technique first.
Do not leave cleaning products on the plastic parts for long periods of time.
Do not apply cleaning products in direct sunlight or at high temperatures.
Glass part cleaning.
Recommended cleaning products:
Mild soap.
Warm water.
Soft cloth/no abrasives.
Sponge.
Cleaning with water.
Pollution can significantly alter luminaire lighting performances.
We recommend regular cleaning of the module reflectors and to check that the radiators are not obstructed.
TRIGGER CURRENT
ECLATEC S.A.S. 41, rue Lafayette - CS 20069 - Maxéville - 54528 LAXOU CEDEX - France
Tel. • + 33 (0)3 83 39 38 00
Site • www.eclatec.com
Number of power supplies per Type B circuit-breaker |  |  | 
Rated Vac (V) | 32 A | 50 A | 63 A
220 | 2 | 3 | 4
400 | 2+2+2 | 3+3+3 | 4+4+4
Number of power supplies per type C circuit-breaker |  |  | 
Rated Vac (V) | 32 A | 50 A | 63 A
220 | 2 | 3 | 4
400 | 2+2+2 | 4+4+4 | 5+5+5
Number of power supplies per type D circuit-breaker |  |  | 
Rated Vac (V) | 32 A | 50 A | 63 A
220 | 2 | 3 | 4
400 | 3+3+3 | 4+4+4 | 6+6+6